## 정류기
형 명 | ESP100(+) | 제조일자 | 2023.10.21 |  | 점검 형태 | 화재예방 점검활동 |  | 수 량 | 9
점검일 | 업체명 | 설치장소 | 셀 | 전압(V) | 내부저항(mΩ) | 비중 | 온도 | 참고값(mΩ) | 비고
2024-07-16 | 양림휴먼시아2단지 | 정류기 | 1 | 12.93 | 3.7 |  |  | 3.3 | 112.1%
2024-07-16 | 양림휴먼시아2단지 | 정류기 | 2 | 12.91 | 3.59 |  |  | 3.3 | 108.8%
2024-07-16 | 양림휴먼시아2단지 | 정류기 | 3 | 12.93 | 3.66 |  |  | 3.3 | 110.9%
2024-07-16 | 양림휴먼시아2단지 | 정류기 | 4 | 12.95 | 3.82 |  |  | 3.3 | 115.8%
2024-07-16 | 양림휴먼시아2단지 | 정류기 | 5 | 12.94 | 3.74 |  |  | 3.3 | 113.3%
2024-07-16 | 양림휴먼시아2단지 | 정류기 | 6 | 12.94 | 3.79 |  |  | 3.3 | 114.8%
2024-07-16 | 양림휴먼시아2단지 | 정류기 | 7 | 12.93 | 3.62 |  |  | 3.3 | 109.7%
2024-07-16 | 양림휴먼시아2단지 | 정류기 | 8 | 12.95 | 3.76 |  |  | 3.3 | 113.9%
2024-07-16 | 양림휴먼시아2단지 | 정류기 | 9 | 12.94 | 3.57 |  |  | 3.3 | 108.2%
[8 empty] | 3.3 | 0%
[8 empty] | 3.3 | 0%
[8 empty] | 3.3 | 0%
[8 empty] | 3.3 | 0%
[8 empty] | 3.3 | 0%
[8 empty] | 3.3 | 0%
[8 empty] | 3.3 | 0%
[8 empty] | 3.3 | 0%
[8 empty] | 3.3 | 0%
[8 empty] | 3.3 | 0%
[8 empty] | 3.3 | 0%
[8 empty] | 3.3 | 0%
[8 empty] | 3.3 | 0%
[8 empty] | 3.3 | 0%
[8 empty] | 3.3 | 0%
[8 empty] | 3.3 | 0%
[8 empty] | 3.3 | 0%
[8 empty] | 3.3 | 0%
[8 empty] | 3.3 | 0%
[8 empty] | 3.3 | 0%
[8 empty] | 3.3 | 0%
0 | 0 | 0 | 31 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 32 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 33 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 34 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 35 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 36 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 37 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 38 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 39 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 40 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 41 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 42 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 43 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 44 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 45 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 46 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 47 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 48 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 49 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 50 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 51 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 52 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 53 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 54 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 55 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 56 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 57 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 58 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 59 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 60 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 61 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 62 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 63 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 64 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 65 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 66 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 67 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 68 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 69 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 70 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 71 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 72 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 73 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 74 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 75 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 76 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 77 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 78 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 79 |  |  |  |  | 3.3 | 0%
0 | 0 | 0 | 80 |  |  |  |  | 3.3 | 0%
|  |  |  | 12.95 | 3.82 |  |  |  | 115.8%
|  |  |  | 12.91 | 3.57 |  |  |  | 108.2%
설치 일자 | 2023.11.28 |  |  |  | 화재 예방 점검 현황 | 설치 상태 | 양 호
[6 empty] | 누액발생 유무 | 양 호
점검 내용 | 1. 전압 상향 조정 필요 116.42V → 119.6V(13.29V/Cell) 그 외 특이사항 없음 2. 조임상태 양호, 온도 관리 요청 |  |  |  |  | 볼트체결 상태 | 양 호
[6 empty] | 연결케이블 상태 | 양 호
[6 empty] | 메인케이블 상태 | 케이블 보호관 없음
조치사항 | 점검결과 내용 통보 |  |  |  |  | 온도 관리 | 관리 필요(주변 30℃, B/T 28~30℃)
[6 empty] | 환기 상태 | 양 호
기타
첨 부
Formulas:
형 명 = [형 명, row above]

## 비상발전기
형 명 | ESP200(+) | 제조일자 | 2023.10.15 |  | 점검 형태 | 화재예방 점검활동 |  | 수 량 | 2
점검일 | 업체명 | 설치장소 | 셀 | 전압(V) | 내부저항(mΩ) | 비중 | 온도 | 참고값(mΩ) | 비고
2024-07-16 | 양림휴먼시아2단지 | 비상발전기 | 1 | 13.01 | 2.12 |  |  | 2.3 | 92.17%
2024-07-16 | 양림휴먼시아2단지 | 비상발전기 | 2 | 13.08 | 2.11 |  |  | 2.3 | 91.74%
#REF! | #REF! | #REF! | 5 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 6 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 7 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 8 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 9 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 10 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 11 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 12 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 13 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 14 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 15 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 16 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 17 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 18 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 19 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 20 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 21 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 22 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 23 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 24 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 25 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 26 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 27 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 28 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 29 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 30 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 31 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 32 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 33 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 34 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 35 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 36 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 37 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 38 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 39 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 40 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 41 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 42 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 43 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 44 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 45 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 46 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 47 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 48 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 49 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 50 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 51 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 52 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 53 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 54 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 55 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 56 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 57 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 58 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 59 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 60 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 61 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 62 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 63 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 64 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 65 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 66 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 67 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 68 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 69 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 70 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 71 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 72 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 73 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 74 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 75 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 76 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 77 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 78 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 79 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 80 |  |  |  |  | #REF! | #REF!
|  |  |  | 13.08 | 2.12 |  |  |  | 92.17%
|  |  |  | 13.01 | 2.11 |  |  |  | 91.74%
설치 일자 | 2023.11.28 |  |  |  | 화재 예방 점검 현황 | 설치 상태
[6 empty] | 누액발생 유무 | 양 호
점검 내용 | 1. 전압 상향 조정 및 온도 관리 요청 |  |  |  |  | 볼트체결 상태 | 양 호
[6 empty] | 연결케이블 상태 | 양 호
[6 empty] | 메인케이블 상태 | 양 호
조치사항 | 점검결과 내용 통보 |  |  |  |  | 온도 관리 | 주변 30℃, B/T 30℃
[6 empty] | 환기 상태 | 양 호
[6 empty] | 기타 | 외부 보호판
첨 부
Formulas:
형 명 = [형 명, row above]

## 방송장비
형 명 | ESP200(+) | 제조일자 | 2023.10.14 |  | 점검 형태 | 화재예방 점검활동 |  | 수 량 | 4
점검일 | 업체명 | 설치장소 | 셀 | 전압(V) | 내부저항(mΩ) | 비중 | 온도 | 참고값(mΩ) | 비고
2024-07-16 | 양림휴먼시아2단지 | 방송장비 | 1 | 13.36 | 2.16 |  |  | 2.3 | 93.91%
2024-07-16 | 양림휴먼시아2단지 | 방송장비 | 2 | 13.23 | 2.14 |  |  | 2.3 | 93.04%
#REF! | #REF! | #REF! | 5 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 6 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 7 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 8 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 9 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 10 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 11 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 12 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 13 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 14 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 15 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 16 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 17 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 18 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 19 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 20 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 21 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 22 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 23 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 24 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 25 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 26 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 27 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 28 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 29 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 30 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 31 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 32 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 33 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 34 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 35 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 36 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 37 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 38 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 39 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 40 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 41 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 42 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 43 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 44 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 45 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 46 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 47 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 48 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 49 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 50 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 51 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 52 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 53 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 54 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 55 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 56 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 57 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 58 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 59 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 60 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 61 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 62 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 63 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 64 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 65 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 66 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 67 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 68 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 69 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 70 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 71 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 72 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 73 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 74 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 75 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 76 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 77 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 78 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 79 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 80 |  |  |  |  | #REF! | #REF!
|  |  |  | 13.36 | 2.16 |  |  |  | 93.91%
|  |  |  | 13.23 | 2.14 |  |  |  | 93.04%
설치 일자 | 2023.12 |  |  |  | 화재 예방 점검 현황 | 설치 상태
[6 empty] | 누액발생 유무 | 양 호
점검 내용 | 1. 전압, 내부저항 이상없으나, 나무 재질 외함 내 설치, 2단 설치로 하단 배터리 점검 어려움, 설치 형태 변경 요청 |  |  |  |  | 볼트체결 상태 | 양 호
[6 empty] | 연결케이블 상태 | 양 호
[6 empty] | 메인케이블 상태 | 양 호
조치사항 | 점검결과 내용 통보 |  |  |  |  | 온도 관리 | 주변 30℃, B/T 30℃
[6 empty] | 환기 상태 | 양 호
[6 empty] | 기타 | 외부 보호판
첨 부
Formulas:
형 명 = [형 명, row above]