## 용복터널
형 명 | RP35(+) | 제조일자 | 2022.07.26 |  | 점검 형태 | BS |  | 수 량 | 16
점검일 | 업체명 | 설치장소 | 셀 | 전압(V) | 내부저항(mΩ) | 비중 | 온도 | 참고값(mΩ) | 비고
2023-09-19 | 용복터널 | UPS 5KVA | 1 | 13.25 | 8.49 |  | 23 |  | #DIV/0!
2023-09-19 | 용복터널 | UPS 5KVA | 2 | 13.3 | 8.44 |  | 23 |  | #DIV/0!
2023-09-19 | 용복터널 | UPS 5KVA | 3 | 13.32 | 8.53 |  | 23 |  | #DIV/0!
2023-09-19 | 용복터널 | UPS 5KVA | 4 | 13.31 | 8.65 |  | 23 |  | #DIV/0!
2023-09-19 | 용복터널 | UPS 5KVA | 5 | 13.26 | 8.61 |  | 23 |  | #DIV/0!
2023-09-19 | 용복터널 | UPS 5KVA | 6 | 13.31 | 8.5 |  | 23 |  | #DIV/0!
2023-09-19 | 용복터널 | UPS 5KVA | 7 | 13.32 | 8.61 |  | 23 |  | #DIV/0!
2023-09-19 | 용복터널 | UPS 5KVA | 8 | 13.33 | 8.59 |  | 23 |  | #DIV/0!
2023-09-19 | 용복터널 | UPS 5KVA | 9 | 13.26 | 8.58 |  | 23 |  | #DIV/0!
2023-09-19 | 용복터널 | UPS 5KVA | 10 | 13.32 | 8.68 |  | 23 |  | #DIV/0!
2023-09-19 | 용복터널 | UPS 5KVA | 11 | 13.33 | 8.55 |  | 23 |  | #DIV/0!
2023-09-19 | 용복터널 | UPS 5KVA | 12 | 13.33 | 8.71 |  | 23 |  | #DIV/0!
2023-09-19 | 용복터널 | UPS 5KVA | 13 | 13.29 | 8.61 |  | 23 |  | #DIV/0!
2023-09-19 | 용복터널 | UPS 5KVA | 14 | 13.34 | 8.4 |  | 23 |  | #DIV/0!
2023-09-19 | 용복터널 | UPS 5KVA | 15 | 13.34 | 8.61 |  | 23 |  | #DIV/0!
2023-09-19 | 용복터널 | UPS 5KVA | 16 | 13.34 | 8.61 |  | 23 |  | #DIV/0!
2023-09-19 | 용복터널 | UPS 5KVA | 17 | [5 empty] | #DIV/0!
2023-09-19 | 용복터널 | UPS 5KVA | 18 | [5 empty] | #DIV/0!
2023-09-19 | 용복터널 | UPS 5KVA | 19 | [5 empty] | #DIV/0!
2023-09-19 | 용복터널 | UPS 5KVA | 20 | [5 empty] | #DIV/0!
2023-09-19 | 용복터널 | UPS 5KVA | 21 | [5 empty] | #DIV/0!
2023-09-19 | 용복터널 | UPS 5KVA | 22 | [5 empty] | #DIV/0!
2023-09-19 | 용복터널 | UPS 5KVA | 23 | [5 empty] | #DIV/0!
2023-09-19 | 용복터널 | UPS 5KVA | 24 | [5 empty] | #DIV/0!
2023-09-19 | 용복터널 | UPS 5KVA | 25 | [5 empty] | #DIV/0!
2023-09-19 | 용복터널 | UPS 5KVA | 26 | [5 empty] | #DIV/0!
2023-09-19 | 용복터널 | UPS 5KVA | 27 | [5 empty] | #DIV/0!
2023-09-19 | 용복터널 | UPS 5KVA | 28 | [5 empty] | #DIV/0!
2023-09-19 | 용복터널 | UPS 5KVA | 29 | [5 empty] | #DIV/0!
#REF! | #REF! | #REF! | 31 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 32 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 33 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 34 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 35 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 36 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 37 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 38 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 39 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 40 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 41 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 42 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 43 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 44 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 45 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 46 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 47 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 48 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 49 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 50 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 51 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 52 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 53 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 54 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 55 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 56 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 57 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 58 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 59 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 60 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 61 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 62 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 63 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 64 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 65 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 66 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 67 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 68 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 69 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 70 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 71 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 72 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 73 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 74 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 75 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 76 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 77 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 78 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 79 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 80 |  |  |  |  | #REF! | #REF!
|  |  |  | 13.34 | 8.71 |  |  |  | #DIV/0!
|  |  |  | 13.25 | 8.4 |  |  |  | #DIV/0!
설치 일자 | 2022.10.15 |  |  |  | 화재 예방 점검 현황 | 설치 상태 | 양 호
[6 empty] | 누액발생 유무 | 양 호
점검 내용 | 1. 배터리 상태 양호, 충전전압 하향 조정 필요(13.10V/Cell) |  |  |  |  | 볼트체결 상태 | 양 호
[6 empty] | 연결케이블 상태 | 양 호
[6 empty] | 메인케이블 상태 | 케이블 보호관 없음
조치사항 | 점검결과 내용 통보 |  |  |  |  | 온도 관리 | 양 호(23도)
[6 empty] | 환기 상태 | 양 호
[6 empty] | 기타 | 에어컨 1대, 소화기 2대
첨 부
Formulas:
형 명 = [형 명, row above]

## 대둔터널
형 명 | RP35(+) | 제조일자 | 2023.01.07 |  | 점검 형태 | BS |  | 수 량 | 18
점검일 | 업체명 | 설치장소 | 셀 | 전압(V) | 내부저항(mΩ) | 비중 | 온도 | 참고값(mΩ) | 비고
2023-09-19 | 대둔터널 | UPS 5KVA | 1 | 13.14 | 8.44 |  | 30 |  | #DIV/0!
2023-09-19 | 대둔터널 | UPS 5KVA | 2 | 13.17 | 8.47 |  | 30 |  | #DIV/0!
2023-09-19 | 대둔터널 | UPS 5KVA | 3 | 13.07 | 8.51 |  | 30 |  | #DIV/0!
2023-09-19 | 대둔터널 | UPS 5KVA | 4 | 13.11 | 8.21 |  | 30 |  | #DIV/0!
2023-09-19 | 대둔터널 | UPS 5KVA | 5 | 13.07 | 8.56 |  | 30 |  | #DIV/0!
2023-09-19 | 대둔터널 | UPS 5KVA | 6 | 13.07 | 8.49 |  | 30 |  | #DIV/0!
2023-09-19 | 대둔터널 | UPS 5KVA | 7 | 13.18 | 8.35 |  | 30 |  | #DIV/0!
2023-09-19 | 대둔터널 | UPS 5KVA | 8 | 13.16 | 8.38 |  | 30 |  | #DIV/0!
2023-09-19 | 대둔터널 | UPS 5KVA | 9 | 13.15 | 8.46 |  | 30 |  | #DIV/0!
2023-09-19 | 대둔터널 | UPS 5KVA | 10 | 13.2 | 8.38 |  | 30 |  | #DIV/0!
2023-09-19 | 대둔터널 | UPS 5KVA | 11 | 13.13 | 8.27 |  | 30 |  | #DIV/0!
2023-09-19 | 대둔터널 | UPS 5KVA | 12 | 13.18 | 8.42 |  | 30 |  | #DIV/0!
2023-09-19 | 대둔터널 | UPS 5KVA | 13 | 13.17 | 8.57 |  | 30 |  | #DIV/0!
2023-09-19 | 대둔터널 | UPS 5KVA | 14 | 13.08 | 8.58 |  | 30 |  | #DIV/0!
2023-09-19 | 대둔터널 | UPS 5KVA | 15 | 13.17 | 8.44 |  | 30 |  | #DIV/0!
2023-09-19 | 대둔터널 | UPS 5KVA | 16 | 13.18 | 8.46 |  | 30 |  | #DIV/0!
2023-09-19 | 대둔터널 | UPS 5KVA | 17 | 13.09 | 8.76 |  | 30 |  | #DIV/0!
2023-09-19 | 대둔터널 | UPS 5KVA | 18 | 13.11 | 8.46 |  | 30 |  | #DIV/0!
2023-09-19 | 대둔터널 | UPS 5KVA | 19 | [5 empty] | #DIV/0!
2023-09-19 | 대둔터널 | UPS 5KVA | 20 | [5 empty] | #DIV/0!
2023-09-19 | 대둔터널 | UPS 5KVA | 21 | [5 empty] | #DIV/0!
2023-09-19 | 대둔터널 | UPS 5KVA | 22 | [5 empty] | #DIV/0!
2023-09-19 | 대둔터널 | UPS 5KVA | 23 | [5 empty] | #DIV/0!
2023-09-19 | 대둔터널 | UPS 5KVA | 24 | [5 empty] | #DIV/0!
2023-09-19 | 대둔터널 | UPS 5KVA | 25 | [5 empty] | #DIV/0!
2023-09-19 | 대둔터널 | UPS 5KVA | 26 | [5 empty] | #DIV/0!
2023-09-19 | 대둔터널 | UPS 5KVA | 27 | [5 empty] | #DIV/0!
2023-09-19 | 대둔터널 | UPS 5KVA | 28 | [5 empty] | #DIV/0!
2023-09-19 | 대둔터널 | UPS 5KVA | 29 | [5 empty] | #DIV/0!
#REF! | #REF! | #REF! | 31 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 32 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 33 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 34 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 35 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 36 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 37 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 38 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 39 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 40 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 41 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 42 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 43 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 44 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 45 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 46 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 47 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 48 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 49 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 50 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 51 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 52 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 53 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 54 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 55 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 56 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 57 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 58 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 59 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 60 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 61 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 62 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 63 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 64 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 65 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 66 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 67 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 68 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 69 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 70 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 71 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 72 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 73 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 74 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 75 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 76 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 77 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 78 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 79 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 80 |  |  |  |  | #REF! | #REF!
|  |  |  | 13.2 | 8.76 |  |  |  | #DIV/0!
|  |  |  | 13.07 | 8.21 |  |  |  | #DIV/0!
설치 일자 | 2023.01 |  |  |  | 화재 예방 점검 현황 | 설치 상태 | 양 호
[6 empty] | 누액발생 유무 | 양 호
점검 내용 | 1. 배터리 상태 양호, Bypass 경보 상태 |  |  |  |  | 볼트체결 상태 | 양 호
[6 empty] | 연결케이블 상태 | 양 호
[6 empty] | 메인케이블 상태 | 케이블 보호관 없음
조치사항 | 점검결과 내용 통보 |  |  |  |  | 온도 관리 | 미 흡(30도)
[6 empty] | 환기 상태 | 양 호
기타
첨 부
Formulas:
형 명 = [형 명, row above]

## 앞대산터널
형 명 | ESP40 | 제조일자 | 2021.11.05 |  | 점검 형태 | BS |  | 수 량 | 16
점검일 | 업체명 | 설치장소 | 셀 | 전압(V) | 내부저항(mΩ) | 비중 | 온도 | 참고값(mΩ) | 비고
2023-09-19 | 앞대산터널 | UPS 10KVA | 1 | 13.16 | 8.21 |  | 31 |  | #DIV/0!
2023-09-19 | 앞대산터널 | UPS 10KVA | 2 | 13.17 | 8.44 |  | 31 |  | #DIV/0!
2023-09-19 | 앞대산터널 | UPS 10KVA | 3 | 13.14 | 8.22 |  | 31 |  | #DIV/0!
2023-09-19 | 앞대산터널 | UPS 10KVA | 4 | 13.2 | 8.31 |  | 31 |  | #DIV/0!
2023-09-19 | 앞대산터널 | UPS 10KVA | 5 | 13.2 | 8.48 |  | 31 |  | #DIV/0!
2023-09-19 | 앞대산터널 | UPS 10KVA | 6 | 13.18 | 8.4 |  | 31 |  | #DIV/0!
2023-09-19 | 앞대산터널 | UPS 10KVA | 7 | 13.22 | 8.68 |  | 31 |  | #DIV/0!
2023-09-19 | 앞대산터널 | UPS 10KVA | 8 | 13.17 | 8.38 |  | 31 |  | #DIV/0!
2023-09-19 | 앞대산터널 | UPS 10KVA | 9 | 공간 협소로 측정 불가 |  |  | 31 |  | #DIV/0!
2023-09-19 | 앞대산터널 | UPS 10KVA | 10 | 공간 협소로 측정 불가 |  |  | 31 |  | #DIV/0!
2023-09-19 | 앞대산터널 | UPS 10KVA | 11 | 13.21 | 8.43 |  | 31 |  | #DIV/0!
2023-09-19 | 앞대산터널 | UPS 10KVA | 12 | 13.19 | 8.14 |  | 31 |  | #DIV/0!
2023-09-19 | 앞대산터널 | UPS 10KVA | 13 | 공간 협소로 측정 불가 |  |  | 31 |  | #DIV/0!
2023-09-19 | 앞대산터널 | UPS 10KVA | 14 | 공간 협소로 측정 불가 |  |  | 31 |  | #DIV/0!
2023-09-19 | 앞대산터널 | UPS 10KVA | 15 | 공간 협소로 측정 불가 |  |  | 31 |  | #DIV/0!
2023-09-19 | 앞대산터널 | UPS 10KVA | 16 | 공간 협소로 측정 불가 |  |  | 31 |  | #DIV/0!
2023-09-19 | 앞대산터널 | UPS 10KVA | 17 | [5 empty] | #DIV/0!
2023-09-19 | 앞대산터널 | UPS 10KVA | 18 | [5 empty] | #DIV/0!
2023-09-19 | 앞대산터널 | UPS 10KVA | 19 | [5 empty] | #DIV/0!
2023-09-19 | 앞대산터널 | UPS 10KVA | 20 | [5 empty] | #DIV/0!
2023-09-19 | 앞대산터널 | UPS 10KVA | 21 | [5 empty] | #DIV/0!
2023-09-19 | 앞대산터널 | UPS 10KVA | 22 | [5 empty] | #DIV/0!
2023-09-19 | 앞대산터널 | UPS 10KVA | 23 | [5 empty] | #DIV/0!
2023-09-19 | 앞대산터널 | UPS 10KVA | 24 | [5 empty] | #DIV/0!
2023-09-19 | 앞대산터널 | UPS 10KVA | 25 | [5 empty] | #DIV/0!
2023-09-19 | 앞대산터널 | UPS 10KVA | 26 | [5 empty] | #DIV/0!
2023-09-19 | 앞대산터널 | UPS 10KVA | 27 | [5 empty] | #DIV/0!
2023-09-19 | 앞대산터널 | UPS 10KVA | 28 | [5 empty] | #DIV/0!
2023-09-19 | 앞대산터널 | UPS 10KVA | 29 | [5 empty] | #DIV/0!
#REF! | #REF! | #REF! | 31 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 32 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 33 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 34 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 35 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 36 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 37 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 38 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 39 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 40 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 41 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 42 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 43 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 44 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 45 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 46 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 47 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 48 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 49 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 50 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 51 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 52 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 53 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 54 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 55 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 56 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 57 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 58 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 59 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 60 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 61 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 62 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 63 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 64 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 65 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 66 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 67 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 68 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 69 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 70 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 71 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 72 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 73 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 74 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 75 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 76 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 77 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 78 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 79 |  |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | 80 |  |  |  |  | #REF! | #REF!
|  |  |  | 13.22 | 8.68 |  |  |  | #DIV/0!
|  |  |  | 13.14 | 8.14 |  |  |  | #DIV/0!
설치 일자 | 2022.10.15 |  |  |  | 화재 예방 점검 현황 | 설치 상태 | 양 호
[6 empty] | 누액발생 유무 | 양 호
점검 내용 | 1. 배터리 상태 양호, 충전전압 상향 조정 필요(13.32V/Cell) |  |  |  |  | 볼트체결 상태 | 양 호
[6 empty] | 연결케이블 상태 | 양 호
[6 empty] | 메인케이블 상태 | 케이블 보호관 없음
조치사항 | 점검결과 내용 통보 |  |  |  |  | 온도 관리 | 미 흡(31도)
[6 empty] | 환기 상태 | 양 호
기타
첨 부
Formulas:
형 명 = [형 명, row above]